| # MEETING |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Minutes of meeting n° 11 |  |  |  | 11 |  |  | 28/01/2026 |  |  |  |  |  |
| Location : Penta Hotel City Center - Brussels |  |  |  |  |  |  |  |  |  |  |  |  |
| Distribution on 28/01/2025 |  |  |  |  |  |  |  |  |  |  |  |  |
| Attendance | Present | Excused | Invited |  | Diffusion |  |  |  | Present | Excused | Invited | Diffusion |
| MO – Penta Hotel City Centre Menno de Richemont | X |  | X |  | X | Contractor - NTSA Thibault Fayd Site supervisor (APO) |  |  | X | X | X X | X X |
| MOD – Immo-Pro (IP) Olivier Fournier (OFO) Leonardo Stefani (LST) – 0474/015.062 | X | X | X X |  | X X | Contractor – Pro4Finish (P4F) Cedric Van der Burght |  |  | X |  | X | X |
| BET TS – TsfPlus Grégoire Sillen |  | X | X |  | X | HSE coordinator – Whiteforge Abdel Saifi |  |  |  | X | X | X |
| ARCH – De Bouwerij Paul De Mulder Iskra Bilic Sofie | X | X | X X X |  | X X X | Contractor – Betico (BET) Mourad Benja |  |  |  | X | X | X |
| BET – Concept Control (CC) Benoit Lallemand |  | X | X |  | X |  |  |  |  |  |  |  |

Next meeting :

04/02/2026 at 11 :00 – On site Chau. de Charleroi nr. 38, 1060 Brussels

## C General

### C1 Approval of the previous minutes of meeting

Néant

### C2 Information exchange

| From whom | Status | Content | Due date |
| --- | --- | --- | --- |
| ARCH | To send | New compartmentation plans (first draft to be validated) | 31/01/26 |
| ARCH | To send | BOQ for phase 2 and fire doors | 31/01/26 |
| P4F | To Send | Technical datasheet for protective pads around emergency buttons |  |
| P4F | To Send | Technical datasheet for crimp free mortar for the fire sealings along the vertical collector |  |
| P4F | To Send | H&S plan (veiligheids- en gezondheidsplan) | ASAP |
| IP | To Send | Methodology note for the execution of the sprinkler network of phase 2 | 04/02/26 |

### C3 Planning

Planning item

Level +5 - Floor back in service

Level +4 - 05/01/2026: Floor out of service - 23/01/2026: Floor back into service (a delay of 1 to 2 days may occur – IP will follow up with MO)

Level +3 - 22/01/2026: Floor out of service (earlier start with third team) - 06/02/2026: Floor back into service (earlier finish)

Level +2 - 05/02/2026: Floor out of service - 20/02/2026: Floor back into service TBC - Fireproof sealings and painting corridor to be planned from 18/02 to 20/02

Level +1 - 19/02/2026: Floor out of service TBC - 06/03/2026: Floor back into service TBC - Fireproof sealings and painting corridor to be planned from 04/03 to 06/03

Fire detection final audit - 06/02/2026 date confirmed

##### D Discussed subjects

| N° | Title | Subject – General | For whom | Due |
| --- | --- | --- | --- | --- |
| 07.01 | Planning | - New planning to be issued with additional details concerning the fire detection works and finishing works. - New planning was issued on 10/12 | MOD | DONE |

| N° | Title | Subject – Sprinklers | For whom |  | Due |
| --- | --- | --- | --- | --- | --- |
| 06.01 | ANPI | A visit with ANPI is scheduled on the 28/12 to review the current layout and remaining remarks. - Following the visit of ANPI several informal remarks were issued. Those remarks will be taken into account in the quote of phase 2 of the works. |  |  | Pro memorie |
| 11.01 | Planning | The presence of two teams on site permits to start the sprinkler works on level 2 earlier then planned. The subsequent dates for finalizing levels +2 and +1 have been deducted from the current work pace. Those dates will need to be confirmed in the following weeks. |  |  | Pro memorie |

| N° | Title | Subject – Finishings/Architecture | For whom | Due |
| --- | --- | --- | --- | --- |
| 07.01 | Finishing works phase 2 | - MOD will send a quick recap of the works to be included in phase 2 of the finishing works - ARCH and P4F will do the necessary site surveys to provide a bill of quantities - P4F will provide a quote based on that bill of quantities Meeting 07/01/2026 - Bill of quantities for phase 2 will be provided by the end of January. - The relevant finishing details (ceiling mouldings) and colour propositions will be issued by 16/01/2026. Meeting 14/01/26 - MO requests BOQ for the fire doors to be replaced according to the comments of the fire brigade to be separated from the rest to be able to order them asap. ARCH will do as requested. Meeting 21/01/26 - Final BOQ to be sent by ARCH by Monday 26/01/26 at the latest. Meeting 28/01/26 - Final adjustment to be brought to BOQ + measurements of the fire doors. ARCH will provide the final version on 28/01/26. - ARCH will add 10% safety margin on the quantities of the final BOQ’s which will only be used based on detailed measured and validated quantities after execution. - ARCH will check and confirm if the ceiling of the kitchen needs to be HACCP. - P4F will provide its quote by Friday 30/01/26 | MOD ARCH ARCH ARCH ARCH P4F | DONE DONE DONE 28/01/26 ASAP 30/01/26 |
| 07.02 | Ceiling inspection hatches | Due to the installation of the new fire detection system, new inspection hatches are needed on the ground floor and level +8 - P4F has provided a unit price for 40x40 inspection hatches including the cut-out, provision and installation of the hatch. MOD has no remark on the unit price. - The price of the inspection hatches will be included in the finishing works phase 2. - The inspection hatches on the ground floor have already been cut out by the hotel staff (5 holes were cut out). P4F will install the inspection hatches by 05/12. - The contractor Betico will provide a layout of the necessary inspection hatches on level +8. - P4F will install the inspection hatches by Thursday 11/12 EOD, at the latest. Provided that the layout plan was sent before 05/06 to P4F. - ARCH will provide a proposition for the painting works of the ceiling hatches (local detail) to prevent the necessity to paint the whole ceiling. (provided in January 2026) Meeting 07/01/26 - The inspection hatches will be finalized by 16/01/2026 on levels +8 and ground floor. (were finalized by 20/01/26) - Some (+-5) inspection hatches will need to be replaced by a 60x60 format instead of the 40x40 format. The structure above is not suited for the placement of the small format of hatches. Meeting 21/01/26 - Inspection hatches done, the painting will be done according to the decision of the design team. - IP will transfer the proposition of ARCH provided on 20/01/26 to MO for further approval of the design team of the hotel. Meeting 28/01/26 - Design team rejected the design proposal. They request one square covering the ceiling hatch and the surrounding plaster work with an overlap of +-5cm. - On the ground floor MO asks to test the colors RAL7021 and RAL7016. Depending on that test, the rest of the hatches will be painted with the validated color. - On level +8 no painting works necessary at the moment as the ceiling will be repainted after the execution of the sprinkler network. The ceiling color will be painted in RAL9016. | P4F P4F BETICO P4F ARCH P4F | DONE DONE DONE DONE DONE DONE DONE |
| 08.01 | Temporary fire doors and walls | On the request of the fire brigade, a temporary fire door and wall will be installed at the 15m limit in the corridor (dead end). The rooms behind this fire wall will be out of service until the end of the sprinkler works. - P4F will provide a planning for the execution of the works - The doors will be delivered on site around the end January/start of February - The fire wall can already be executed while waiting for the doors (dates to be provided in the planning) - The doors will not be painted. The additional options for the doors are not retained. - The wall will be painted (same color as corridor) on one side only! Meeting 14/01/26: - Gyproc material for the walls is scheduled to be delivered on site on 20/01/26. Date to be confirmed. Meeting 21/01/26: - The wall structure has been started earlier then expected on levels +6 and +7. - The finalization of the walls and doors remains as planned on 13/02/26 | P4F | DONE |
| 08.02 | Painting works +6 | - Painting works in the corridor on lvl+6 were finalized. - Room 609: damaged wall still to be painted. Meeting 21/01/26 - Room 609 will be painted at the same time as the painting for level 4 which is due by the end of this week. | P4F | 23/01/26 |
| 08.03 | Painting works +5 | Painting status of level +5 still needs to be assessed with the architect on site. - P4F will upload the pictures on the shared platform |  | DONE |
| 11.02 | Level +8 preparatory ceiling works | MO requested to already execute the openings in studio 4 which is currently unused. - P4F will communicate a date in the coming weeks for this test. - The floor will need to be protected locally, and the debris will be evacuated immediately. - The ceiling will be opened according to the latest layout proposed on plan by ARCH and NTSA. | P4F | 04/02/26 |
| 11.03 | Protective pads around emergency button | MO asks to place protective pads around the fire emergency buttons in the back of the house. No protective pads necessary on the upper floors. - Technical data sheet to be introduced by P4F. | P4F | ASAP |
| 11.04 | Fireproof sealings | TsfPlus transmitted a remark concerning the fireproof sealings of the vertical collector in the corridor. The sealing executed solely with fireproof foam is not satisfactory. - P4F confirmed the sealing wasn’t finished (foam drying). The different layers are executed as proposed at the start. - P4F will provide the technical datasheet of the crimp free mortar to be validated by ARCH. | P4F |  |

| N° | Title | Subject – Fire detection | For whom |  | Due |
| --- | --- | --- | --- | --- | --- |
| 08.04 | Fire detectors in the rooms | The fire detectors in the rooms are being replaced by fire detectors with integrated alarms. The modification has started and will be finished by Wednesday 14/01/2026, depending on the availability of the rooms. The fire detection system being modified on levels +2, +3, +4, +5, and +6 will be temporarily kept out of service until the 14th of January 2026 in order to prevent warnings on the central unit. The programmer will reinstate the system after the modification. Meeting 14/01/26 - Programming will be organised Friday 16/01. Meeting 21/01/26 - Modification and programming of fire detectors with alarm in the rooms has been finalized. |  |  |  |
| 08.05 | Fire detection controls | Betico awaits the information on all the controls that need to be taken into account. IP will follow up with the engineering office Concept Control to provide the necessary information. Meeting 14/01/2026: - List of fire detection controls will be setup by Betico and sent to IP and MO. - Concept Control will provide the necessary information to complete the list and relevant actions in order to be compliant. |  | IP BET CC | DONE 23/01/26 23/01/26 |
| 08.06 | Communication with central unit of the parking | IP will contact the parking to know the position of the central unit which needs to be connected to the central unit of the hotel. Meeting 14/01/26: - Betico will account for a cable (8-cables), that can be used by the parking as well which will prevent that the parking needs to place a separate cable. The change order will be sent as soon as the local measurements are done. |  | IP | 16/01/26 |
| 09.01 | Extra keys | MO has requested new keys for the fire central and “repetitor”. Betico will provide the price for those extra keys. |  | BET | 21/01/26 |

## E. Appendices

Indications on plan, see sketch here under:

## F. General remarks

This report will be subject to approval at the beginning of the next meeting; however, any corrections may be made upon receipt of it.

End of this report.